## System 1_IDU_Specifications
Item | Value |  | Unit |  | Value | Unit
Series name |  |  | － |  |  | －
Model designation |  |  | － |  |  | －
Noise (sound pressure level) (high) | 36 |  | dB(A) |  | 36 | dB(A)
Noise (sound pressure level) (medium) | 31 |  | dB(A) |  | 33 | dB(A)
Noise (sound pressure level) (low) | 25 |  | dB(A) |  | 28 | dB(A)
Rated voltage | 220-240 |  | V |  | 220-240 | V
Rated frequency | 50 |  | Hz |  | 50 | Hz
Phase | 1 |  | － |  | 1 | －
Power cable (core) | 3 |  | N |  | 3 | N
Circuit breaker capacity | 6 |  | A |  | 6 | A
MOP | — |  | A |  | — | A
MCA | — |  | A |  | — | A
Consumed power | 0,03 |  | kW |  | 0,03 | kW
Refrigerant type | R410A |  | － |  | R410A | －
Standard controller | — |  | － |  | — | －
Optional controller | — |  | － |  | — | －
Connection method | Flare Connection |  | － |  | Flare Connection | －
IDU loading quantity (40') | 378 |  | unit |  | 378 | unit
IDU loading quantity (40' HQ) | 432 |  | unit |  | 432 | unit
Item | Metric system |  | Metric Unit |  | Metric system | Metric Unit
Cooling capacity | 2,2 |  | kW |  | 2,8 | kW
Heating capacity | 2,5 | 2,5 | kW |  | 3,2 | kW
Airflow (high) | 500 | 500 | m3/h |  | 570 | m3/h
Airflow (medium) | 460 | 460 | m3/h | m3/h | 480 | m3/h
Airflow (low) | 370 | 370 | m3/h | m3/h | 420 | m3/h
Static pressure outside the unit | 0 | 0 | Pa | Pa | 0 | Pa
Cross-sectional area of power line conductor | 1 | 1 | mm2 | mm2 | 1 | mm2
Dimension of gas pipe | Φ9.52 | Φ9.52 | mm | mm | Φ9.52 | mm
Dimension of liquid pipe | Φ6.35 | Φ6.35 | mm | mm | Φ6.35 | mm
Connection method | Flare Connection | Flare Connection | － | － | Flare Connection | －
Outline dimensions (main body) (W) | 570 | 570 | mm | mm | 570 | mm
Condensing pipe (outer diameter) | φ25 | φ25 | mm | mm | φ25 | mm
Outline dimensions (main body) (D) | 570 | 570 | mm | mm | 570 | mm
Condensing pipe (wall thickness) | 2,5 | 2,5 | mm | mm | 2,5 | mm
Outline dimensions (main body) (H) | 265 | 265 | mm | mm | 265 | mm
Outline dimensions (front panel) (W) | 698 | 698 | mm | mm | 698 | mm
Outline dimensions (front panel) (D) | 698 | 698 | mm | mm | 698 | mm
Outline dimensions (front panel) (H) | 110 | 110 | mm | mm | 110 | mm
Package dimensions (main body) (L) | 695 | 695 | mm | mm | 695 | mm
Package dimensions (main body) (W) | 650 | 650 | mm | mm | 650 | mm
Package dimensions (main body) (H) | 280 | 280 | mm | mm | 280 | mm
Package dimensions (front panel) (L) | 620 | 620 | mm | mm | 620 | mm
Package dimensions (front panel) (W) | 620 | 620 | mm | mm | 620 | mm
Package dimensions (front panel) (H) | 47,5 | 47,5 | mm | mm | 47,5 | mm
Net weight (main body) | 17,5 | 17,5 | kg | kg | 17,5 | kg
Net weight (front panel) | 3 | 3 | kg | kg | 3 | kg
Gross weight (main body) | 22,5 | 22,5 | kg | kg | 22,5 | kg
Gross weight (front panel) | 4,5 | 4,5 | kg | kg | 4,5 | kg
Item | Value |  | Unit |  | Value | Unit
Series name |  |  | － |  |  | －
Model designation |  |  | － |  |  | －
Noise (sound pressure level) (high) | 43 |  | dB(A) |  | 35 | dB(A)
Noise (sound pressure level) (medium) | 41 |  | dB(A) |  | 33 | dB(A)
Noise (sound pressure level) (low) | 39 |  | dB(A) |  | 30 | dB(A)
Rated voltage | 220-240 |  | V |  | 220-240 | V
Rated frequency | 50 |  | Hz |  | 50 | Hz
Phase | 1 |  | － |  | 1 | －
Power cable (core) | 3 |  | N |  | 3 | N
Circuit breaker capacity | 6 |  | A |  | 6 | A
MOP | — |  | A |  | / | A
MCA | — |  | A |  | / | A
Consumed power | 0,045 |  | kW |  | / | kW
Refrigerant type | R410A |  | － |  | R410A | －
Standard controller | — |  | － |  | YAP1F | －
Optional controller | — |  | － |  | XK46/XK79/YV1L1 | －
Connection method | Flare Connection |  | － |  | Flare Connection | －
IDU loading quantity (40') | 378 |  | unit |  | 576 | unit
IDU loading quantity (40' HQ) | 432 |  | unit |  | 576 | unit
Item | Metric system |  | Metric Unit |  | Metric system | Metric Unit
Cooling capacity | 5,6 |  | kW |  | 2,8 | kW
Heating capacity | 6,3 |  | kW |  | 3,2 | kW
Airflow (high) | 730 |  | m3/h |  | 500 | m3/h
Airflow (medium) | 650 |  | m3/h |  | 440 | m3/h
Airflow (low) | 560 |  | m3/h |  | 300 | m3/h
Static pressure outside the unit | 0 |  | Pa |  | 0 | Pa
Cross-sectional area of power line conductor | 1 |  | mm2 |  | 1 | mm2
Dimension of gas pipe | Φ15.9 |  | mm |  | Φ9.52 | mm
Dimension of liquid pipe | Φ9.52 |  | mm |  | Φ6.35 | mm
Connection method | Flare Connection |  | － |  | Flare Connection | －
Outline dimensions (main body) (W) | 570 |  | mm |  | 845 | mm
Condensing pipe (outer diameter) | φ25 |  | mm |  | Φ20 | mm
Outline dimensions (main body) (D) | 570 |  | mm |  | 209 | mm
Condensing pipe (wall thickness) | 2,5 |  | mm |  | 1,5 | mm
Outline dimensions (main body) (H) | 265 |  | mm |  | 289 | mm
Outline dimensions (front panel) (W) | 698 |  | mm |  | / | mm
Outline dimensions (front panel) (D) | 698 |  | mm |  | / | mm
Outline dimensions (front panel) (H) | 110 |  | mm |  | / | mm
Package dimensions (main body) (L) | 695 |  | mm |  | 973 | mm
Package dimensions (main body) (W) | 650 |  | mm |  | 278 | mm
Package dimensions (main body) (H) | 280 |  | mm |  | 364 | mm
Package dimensions (front panel) (L) | 620 |  | mm |  | / | mm
Package dimensions (front panel) (W) | 620 |  | mm |  | / | mm
Package dimensions (front panel) (H) | 47,5 |  | mm |  | / | mm
Net weight (main body) | 17,5 |  | kg |  | 10,5 | kg
Net weight (front panel) | 3 |  | kg |  | / | kg
Gross weight (main body) | 22,5 |  | kg |  | 12,5 | kg
Gross weight (front panel) | 4,5 |  | kg |  | / | kg

## System 1_ODU_Specifications
Item | Value |  | Unit
Series name |  |  | －
Model designation |  |  | －
Branch model | / |  | －
Static pressure | 110 |  | Pa
Noise (sound pressure level) | / |  | dB(A)
Rated voltage | 380-415 |  | V
Rated frequency | 50 |  | Hz
Phase | 3 |  | －
Power cable (core) | 5 |  | N
Circuit breaker capacity | 50 |  | A
MOP | / |  | A
MCA | / |  | A
Input current for cooling | / |  | A
Input current for heating | / |  | A
Input current for water heating | / |  | A
Maximum current | 49 |  | A
Compressor type 1 |  |  | －
Number of compressors | 2 |  | N
Compressor refrigeration oil type | FV68H |  | －
Maximum working pressure of discharge side | 4,3 |  | MPa
Maximum working pressure of suction side | 2,5 |  | MPa
Maximum allowable pressure | 4,3 |  | MPa
Working capacity regulation range | 6~100 |  | %～%
Number of connectable IDUs at most | 36 |  | unit
Category of electric shock protection | I |  | －
Waterproofing grade | IPX4 |  | --
Climate type |  |  | －
Refrigerant type | R410A |  | －
Refrigerant charge | 8,3 |  | kg
Connection method | Brazing Connection |  | －
ODU loading quantity (40') | 22 |  | unit
ODU loading quantity (40' HQ) | 22 |  | unit
Item | Metric system | Metric system | Metric Unit | Metric Unit
Cooling capacity | 61,5 | 61,5 | kW | kW
Heating capacity | 69 | 69 | kW | kW
Airflow | 16500 | 16500 | m3/h | m3/h
Cross-sectional area of power line conductor | 10 | 10 | mm2 | mm2
Input power for cooling | 27 | 27 | kW | kW
Input power for heating | 24,27 | 24,27 | kW | kW
Input power for water heating | / | / | kW | kW
Maximum input power | 27,41 | 27,41 | kW | kW
Temperature range for cooling | -5~55 | -5~55 | ℃ | ℃
Temperature range for heating | -30~24 | -30~24 | ℃ | ℃
Temperature range for water heating | / | / | ℃ | ℃
Temperature range for cooling + water heating | / | / | ℃ | ℃
Temperature range for heating + water heating | / | / | ℃ | ℃
Temperature range for heat recovery | / | / | ℃ | ℃
Dimension of high pressure gas pipe (connected to IDU) | / | / | mm | mm
Dimension of low pressure gas pipe (connected to IDU) | / | / | mm | mm
Dimension of gas pipe (connected to IDU) | Φ28.6 | Φ28.6 | mm | mm
Dimension of liquid pipe (connected to IDU) | Φ15.9 | Φ15.9 | mm | mm
Dimension of oil balance pipe | / | / | mm | mm
Outline dimensions (W) | 1340 | 1340 | mm | mm
Outline dimensions (D) | 775 | 775 | mm | mm
Outline dimensions (H) | 1690 | 1690 | mm | mm
Package dimensions (L) | 1400 | 1400 | mm | mm
Package dimensions (W) | 830 | 830 | mm | mm
Package dimensions (H) | 1855 | 1855 | mm | mm
Net weight | 355 | 355 | kg | kg
Gross weight | 370 | 370 | kg | kg